## Section 1
C2.2 | The Bill of Quantities
THIS IS NOT A RETURNABLE DOCUMENT
Item | Description | Unit | Quantity | Rate | Amount
No.
Total Brought Forward
BILL OF QUANTITIES
NOTES
In accordance with the NEC3 contract, this is an Option B: Remeasurement priced contract with bill of quantities.
The Employer provides the bill of quantities which is priced by the Contractor.
The contract price is the sum of prices for all items in the bill which may include lump sums for certain items.
When the work is done, if it is found by remeasurement that the estimated quantity is not correct, it is corrected, and payment is made to the Contractor to reflect the actual work conducted.
The monetary amounts that the Contractor fills in, in this document, shall be deemed to be algebraically accurate and fully inclusive of the following:
The monetary amounts that the Contractor fills in, in this document, shall be deemed to be algebraically accurate and fully inclusive of the following:
Inductions, permitting, all SHERQ requirements as per the Employer's requirements, risk assessments by relevant authorities as determined by the Employer and Statutory Bodies, inspections and audits, planning, all Plant and Materials and Equipment required to undertake the complete scope of the works, access requirements for Plant and Materials and Equipment, certification of Equipment and vessels, fuels and lubricants and any other consumables, demolition and disposal of existing materials and equipment, all diving work below water and on the water surface, underwater installation by diving, procurement, offloading, material and equipment handling, storage, fabrication, equipment and infrastructure refurbishment, testing, modifications, welding, bolting, production, corrosion protection, rigging, trial fitting, marking, packing, transportation, mechanical and civil land structural and electrical and control installations, electrical and control system hook-ups and wiring, punch listing, cold and hot commissioning, trial operation, handover and project management and any other requirements not specifically mentioned but required as per industry and engineering and construction legislation and requirements.
SECTION NO 1
PRELIMINARY AND GENERAL
BILL NO.1: PRELIMINARIES
PREAMBLES
Fixed preliminary items
Fixed preliminary items
Fixed preliminary items will be valuated and paid on a proven cost basis up to the total value
A.1 | Fixed Charge Items
Contractual requirements
A.1.1 | All Contractual and legal requirements incl. safety, insurances, compensations | Sum | 1
A.1.2 | Main name and notice board | Sum | 1
A.1.3 | Preparation and Maintenance of Quality Control Plan (QCP) | Sum | 1
A.1.4 | Permits and Site Access | Sum | 1
Establishment of Facilities on Site
A.1.5 | Offices and storage sheds | Sum | 1
A.1.6 | Ablution and latrine facilities | Sum | 1
A.1.7 | Tools and equipment | Sum | 1
A.1.8 | Water supplies, electric power, communications, dealing with water | Sum | 1
A.1.9 | Supply and install electrical connection on site camp | Sum | 1
A.1.10 | Removal of site establishment | Sum | 1
A.1.11 | Rehabilitation of site | Sum | 1
Total Carried Forward
A.1.12 | Health and safety:
| Occupational Health and Safety Act, Construction Regulations, 2003, and the Health and Safety Specification obligations, Maintenance of Health and Safety File and Close out at end of project | Sum | 1
A.1.13 | Health and Safety compliance (incl. PPE, harnesses, etc.) | Sum | 1
A.1.14 | All other fixed-charge obligations | Sum | 1
A.1.15 | Environmental Management Compliance (Compliance to TNPA CEMP, SES and Environmental Legislations) | Sum | 1
A.2 | Time Related Items
A.2.1 | Contractual requirements | Months | 18
Operation and maintenance of facilities on site for duration of contract
A.2.2 | Offices and storage sheds | Months | 18
A.2.3 | Ablution and latrine facilities | Months | 18
A.2.4 | Tools and equipment | Months | 18
Total Carried Forward
A.2.5 | Plant | Months | 18
A.2.6 | Provision of water. electricity & communication | Months | 18
A.2.7 | Supervision for duration of contract | Months | 18
A.2.8 | Company and head office overhead costs for duration of construction | Months | 18
A.2.9 | Other time related obligations | Months | 18
A.2.10 | Provision of on-site security services to safeguard the Contractor's assets and the entire site on a 24-hour basis, seven (7) days per week, for the duration of the contract. | Months | 18
A.2.11 | On site Staff | Months | 18
A.2.12 | Onsite Environmental Officer | Months | 18
Total Carried Forward
A.3 | Enterprise Development (CIDB B.U.I.L.D PROGRAM)
Indirect Targeting for Enterprise Development though Construction Works Contracts, Gazette Notice No.36190 of 25 February 2013
(a) Enterprise Development of Targeted Enterprise or JV partners
A.3.1 | (a.1) Needs Analysis and Enterprise Development Plan per Targeted Enterprise | Item | 1
A.3.2 | (a.2) Monitoring and Interim Reporting per Targeted Enterprise | Per Quarter | 6
A.3.3 | (a.3) Project Completion Report per Targeted Enterprise | Item | 1
A.3.4 | Total (a.1 + a.2 + a.3) | Prov Sum | 1
Total Carried Forward
END OF SECTION 1
Total of Section 1 Carried Forward to Final Summary

## Section 2
THIS IS NOT A RETURNABLE DOCUMENT
Item | Description | Unit | Quantity | Rate | Amount
No.
Total Brought Forward
SECTION NO. 2: CIVIL WORKS
B.1 | BILL NO.1: ALTERATIONS, DEMOLITIONS, ETC
PREAMBLES
The Model Preambles for Trades (2008 edition), as
published by the Association of South African Quantity
Surveyors, shall be deemed to be incorporated in these
bills of quantities and no claims arising from brevity of
description of items, fully described in the said Model
Preambles, will be entertained
The following "Supplementary Preambles" are
incorporated in this bill to satisfy the requirements of the
project and shall take precedence over the provisions of
the said Model Preambles
SUPPLEMENTARY PREAMBLES
General:
The Contractor shall carry out the whole of the works
with as little mess and noise as possible and with a
minimum of disturbance to adjoining premises and their
tenants. He shall provide proper protection and provide,
erect and remove when directed, any temporary
tarpaulins that may be necessary during the progress of
the works, all to the satisfaction of the Employer
Demolitions and Works on Site
Water supply pipes and other piping that may be
encountered and found necessary to disconnect or cut,
shall be effectually stopped off or grubbed up and
removed, and any new connections that may be
necessary shall be made with proper fittings, to the
satisfaction of the Principal Agent
The Contractor will be held solely responsible for any damage to persons and property and for the safety of the structures and must make good at his expense any damage that may occur
All demolitions and works on site must be carried out
carefully and in the safest possible manner and the
Contractor is to make a thorough examination and take
all necessary precautions before proceeding with the
work. The utmost care is to be observed to avoid any
structural or other damage in the remaining portions of
the existing building
Old materials to be carted away
Old materials from the alterations, except where
described as to be re-used or handed over, as well as
all rubbish, etc must be regularly carted from the site
and not be allowed to accumulate on or around the site
Security Fence
Taking down and removal of:
B.1.1 | 2,4 m Steel Palisade Fencing including breaking removing any concrete bases then backfill and make good. Then remove palisade fence to be disposed of at approved dump site(s). | m | 1500
B.1.2 | 2,7 m high security welded mesh Fencing including breaking removing any concrete bases then backfill and make good. Then remove palisade fence to be disposed of at approved dump site(s). | m | 2000
Site Clearance Etc
B.1.3 | Digging up and removing rubbish, debris, vegetation, hedges, shrubs, bush, etc. and trees not exceeding 200mm girth and cart away to prescribed stockpiles on site within 30 km radius | m² | 7000
B.1.4 | Stripping average 150mm thick layer of topsoil and depositing material in prescribed stockpiles on site within 30 km radius | m² | 7000
Total Carried Forward
Service Ducts
B.1.5 | Supply, deliver and install 110dia Upvc Pipes | m | 5000
B.1.6 | Suppl, deliver and install 160dia Upvc Pipes | m | 5000
B.1.7 | Supply, deliver and install Cable Draw Wire | m | 10000
B.1.8 | Supply, deliver and install Cable Marking tape | m | 5000
Protection, Removal and Realignment of Existing Services:
B.1.9 | Underground power cables | m | 300
B.1.10 | Temporary protection of other services | Sum | 1
B.1.11 | Permanent protection of existing services by concrete encasement | Sum | 1
Fencing
B.1.12 | Design, supply, deliver and install complete 2.4 m high security welded mesh fence including 2.7m high intermediate posts and 300mm overhead spikes and all associated accessories. | m | 3500
Total Carried Forward to Section Summary
Item | Description | Unit | Quantity | Rate | Amount
No.
Total Brought Forward
B.2 | BILL NO.2
EARTHWORKS
Carting away of excavated material
Descriptions of carting away of excavated material shall
be deemed to include loading excavated material onto
trucks directly from the excavations or, alternatively,
from stockpiles situated on the building site
Filling
Notwithstanding the reference to prescribed multiple
handling in clause 1 page 6 of the Standard System of
Measuring Building Work, prices for filling and backfilling
shall include for all selection and any necessary multiple
handling of material
Total Carried Forward
Excavation
Excavation in earth not exceeding 2m deep including shaping and trimming for
B.2.1 | Bases | m³ | 140
Extra over trench and hole excavations in earth for excavation in
B.2.2 | Soft rock | m³ | 14
B.2.3 | Hard rock | m³ | 7
Extra over all excavation for carting away
B.2.4 | Surplus material from excavations to prescribed stockpiles within 15km radius | m³ | 140
Risk of collapse of excavations
B.2.5 | Sides of trench and hole excavations not exceeding 1,5m deep | m² | 10500
Excavation in Earth Not Exceeding 2m Deep
B.2.6 | Pipe trenches | m3 | 1300
B.2.7 | Light pole/manhole foundations | m3 | 200
Total Carried Forward
Existing Services
B.2.8 | Excavate by hand in soft material to expose electrical cables | m3 | 300
B.2.9 | Excavate by hand in Hard material to expose electrical cables | m3 | 300
Earthworks
B.2.10 | Imported bedding material | m3 | 600
B.2.11 | Backfilling with excavated material | m3 | 900
B.2.12 | Disposal of surplus material to designated location within 30 kms radius | m3 | 200
Placing And Compacting the Material In 200mm Thickness Lifts (Refer to C3 Scope of works and drawing pack for material specifics)
B.2.13 | Compacting to 90% Mod AASHTO | m3 | 1000
B.2.14 | Compacting to 100% Mod AASHTO | m3 | 500
B.2.15 | Compacting to 93% Mod AASHTO | m3 | 350
Keeping Excavations Free of Water
B.2.16 | Keeping excavations free of all water other than subterranean water | Months | 18
B.2.17 | Underground services survey | Sum | 1
Total Carried Forward
Manholes
B.2.18 | Hand excavation not exceeding 2m in depth | m3 | 40
B.2.19 | Supply and install of precast manhole. 1m diameter 1m depth with lockable lid | No. | 10
Earth filling
B.2.20 | Sub-base course of G5 material in accordance with SABS 1200 DM Compacting to 93% Mod AASHTO | m3 | 40
B.2.21 | Sub-base course of G3 material in accordance with SABS 1200 DM Compacting to 93% Mod AASHTO | m3 | 40
Total Carried Forward to Section Summary
Item | Description | Unit | Quantity | Rate | Amount
No.
Total Brought Forward
BILL NO.3
B.3 | CONCRETE, FORMWORK AND
REINFORCEMENT
The costs of making, storing and testing of concrete test
cubes as required under clause 7 "Tests" of SABS 1200
G shall include the cost of providing cube moulds
necessary for the purpose, for testing costs and for
submitting reports on the tests to the engineer. The
testing shall be undertaken by an independent firm or
institution nominated by the contractor to the approval of
the engineer. (Test cubes are measured separately)
The making, storing and testing of test cubes shall be
carried out according to SANS 5861 and SANS 5862
and the rule for validity of test results shall be in
accordance with SANS 5863. The rule for acceptance of
valid cube results shall be in accordance with SANS
2001- CC1 clause 5.1.2. All valid cube test results shall
be recorded in consecutive or date order and not be
rearranged to influence the outcome of the relevant
rules. Statistical acceptance of the cube results is
issued together with these Bills of Quantities
Formwork to soffits of solid slabs etc shall be deemed to
be to slabs not exceeding 250mm thick unless otherwise
described Formwork to sides of bases, pile caps, ground
beams, etc will only be measured where it is prescribed
by the engineer for design reasons. Formwork
necessitated by irregularity or collapse of excavated
faces will not be measured, and the cost thereof shall be
deemed to be included in the allowance for taking the
risk of collapse of the sides of the excavations, provision
for which is made in "Earthworks
Unreinforced Concrete Cast in Excavated Surfaces
25 MPa/19mm Concrete
B.3.1 | Bases | m³ | 140
Test Cubes
B.3.2 | Making and testing 150 x 150 x 150mm concrete strength test cubes, 3 cubes per load | No. | 70
Rough Formwork
Rough Formwork to:
B.3.3 | Sides of bases | m² | 350
END OF SECTION 2
Total Carried Forward to Section Summary
BILL NO. | SECTION 2 SUMMARY | AMOUNT
B.1 | BILL NO.1: ALTERATIONS, DEMOLITIONS, ETC
B.2 | BILL NO.2: EARTHWORKS
B.3 | BILL NO.3: CONCRETE, FORMWORK AND
REINFORCEMENT
| TOTAL EXCLUDING VAT | R
CARRIED TO FINAL SUMMARY

## Section 3
THIS IS NOT A RETURNABLE DOCUMENT
Item | Description | Unit | Quantity | Rate | Amount
No.
Total Brought Forward
SECTION NO.3: ELECTRICAL
C.1 | BILL NO.1
ELECTRICAL DESIGN, VERIFICATION AND MODELLING
C.1.1 | Verify and adjust the proposed lighting and kiosk drawings/design provided in accordance with SANS and the appropriate lighting requirements to ensure the installation complies with the relevant legislation and regulatory framework standards. | Sum | 1
C.1.2 | Create a lighting simulation and model of the proposed/adjusted lighting installation. | Sum | 1
Total Carried for Section Summary
Item | Description | Unit | Quantity | Rate | Amount
No.
Total Brought Forward
BILL NO 2: LIGHTING
C.2 | ENTRANCE LIGHTING
Supply and install Luminares including all connections, etc., mounted in position including all terminations, aiming and accessories
C.2.1 | Supply, deliver, offload, and install 4 x 12m (above NGL) planted Galvanised steel streetlight poles. | No | 4
C.2.2 | Supply, deliver and install equivalent or similar approved to Marine Grade LUXMO II LED 32 Street Light, 140W, 5000K with bottom entry dual spigot and a 5A 1-phase overcurrent breaker (MCB) SABS Approved, with all required accessories. | No | 8
Total Carried Forward
Distribution Boards
C.2.3 | Design, Supply and Install LV Kiosk with Back-to-Back doors and distribution board including all breakers, mounting accessories, plugs, glands, gland plate, wiring, labelling in the stainless steel 3CR12 enclosure. Powered coated Avo Green with padlock lockable doors (Master Locks included) and inclusive of concrete plinth bases. Each kiosk enclosure should have a Five-sided cage structure (four vertical walls with security gates and a roof). The security mess panel cage system is to be constructed from mild steel and hot dip galvanized for marine environments as per SANS 121/BS EN ISO 1461. The gate system is to be secured with an approved padlock entry system. Clearance should be made so that the Kiosk doors can be opened for operations and maintenance. | No. | 1
Each kiosk should house the following which is to be supplied and installed as well (These DBs are for 3x 9 light circuits; EK8, EK12, EK15 & 2 x 12 light circuits; EK3, EK5):
All components to comply with SABS
-1 x 40A 3-phase isolating Circuit breaker (Large frame)
-3 x 32A 1-phase overload Circuit breaker (MCB)
-2 x 5A 1-phase overload control circuit breaker (MCB)
-1 x 16A photocell IP65
-1 x 3-phase 45A contactor 220V coil
Cabling
C.2.4 | 16mm2 4 core ECC cable | m | 200
Testing And Commissioning
C.2.5 | Testing and Commissioning of complete installation in accordance with SANS 10142-1 including the issue of COC certificates | Sum | 1
Total Carried Forward
Perimeter Lighting
Supply and install Luminares including all connections, etc., mounted in position including all terminations, aiming and accessories
C.2.6 | Supply, deliver, offload, and install 6m above NGL planted galvanised streetlight poles. Poles to be treated with anti-corrosion layer suitable for marine environment | No. | 170
C.2.7 | Supply, deliver and install equivalent or similar approved to Marine Grade LUXMO I LED 4x6 Type Street Light, 107W, 5000K with bottom entry spigot, and a 5A 1-phase overcurrent breaker (MCB) SABS Approved with all required accessories | No. | 170
Total Carried Forward
Distribution Boards
C.2.8 | Design, Supply and Install LV Kiosk with Back-to-Back doors and distribution board including all breakers, mounting accessories, plugs, glands, gland plate, wiring, labelling in the stainless steel 3CR12 enclosure. Powered coated Avo Green with padlock lockable doors (Master Locks included) and inclusive of concrete plinth bases. Each kiosk enclosure should have a Five-sided cage structure (four vertical walls with security gates and a roof). The security mess panel cage system is to be constructed from mild steel and hot dip galvanized for marine environments as per SANS 121/BS EN ISO 1461. The gate system is to be secured with an approved padlock entry system. Clearance should be made so that the Kiosk doors can be opened for operations and maintenance. | No. | 9
Each kiosk should house the following which is to be supplied and installed as well(These DBs are for the 9 x 12 light circuits; EK1, EK2, EK4, EK6,EK7, EK9, EK10, EK11, EK13):
-1 x 200A 3-phase Main Circuit breaker (Large frame) fault level current rating according to contractor design and correct current tripping curve to be selected for installations
-1 x 40A 3-phase isolating Circuit breaker (Large frame)
-3 x 32A 1-phase overload Circuit breaker (MCB)
-2 x 5A 1-phase overload control circuit breaker (MCB)
-1 x 16A photocell IP65
-1 x 3-phase 45A contactor 220V coil
C.2.9 | Design, Supply and Install LV Kiosk with Back-to-Back doors and distribution board including all breakers, mounting accessories, plugs, glands, gland plate, wiring, labelling in the stainless steel 3CR12 enclosure. Powered coated Avo Green with padlock lockable doors (Master Locks included) and inclusive of concrete plinth bases. Each kiosk enclosure should have a Five-sided cage structure (four vertical walls with security gates and a roof). The security mess panel cage system is to be constructed from mild steel and hot dip galvanized for marine environments as per SANS 121/BS EN ISO 1461. The gate system is to be secured with an approved padlock entry system. Clearance should be made so that the Kiosk doors can be opened for operations and maintenance. | No. | 5
Each kiosk should house the following which is to be supplied and installed as well (These DBs are for 3x 9 light circuits; EK8, EK12, EK15 & 2 x 12 light circuits; EK3, EK5):
All components to comply with SABS
-1 x 40A 3-phase isolating Circuit breaker (Large frame)
-3 x 32A 1-phase overload Circuit breaker (MCB)
-2 x 5A 1-phase overload control circuit breaker (MCB)
-1 x 16A photocell IP65
-1 x 3-phase 45A contactor 220V coil
C.2.10 | Supply, deliver and Install 200A 3-phase Main Circuit breaker, Large frame, ( fault level current rating according to contractor design and correct current tripping curve to be selected for installations) inside of new 400V LV Supply Side of the New 200kVA Mini Sub for the 95mm2 4 core ECC cable to supply each lighting circuit, Inclusive of all associated works to install the Circuit Breaker | No. | 4
Total Carried Forward
C.2.11 | Supply and Install 200A 3-phase Main Circuit breaker, large frame, (fault level current rating according to contractor design and correct current tripping curve to be selected for installations) inside of existing 400V LV Minisub for the 95mm2 4 core ECC cable to supply lighting circuit, Inclusive of all associated works to install the Circuit Breaker | No. | 1
Cabling
C.2.12 | 16mm2 4 core ECC cable | m | 5200
C.2.13 | 95mm2 4 core ECC cable | m | 5000
Testing And Commissioning
C.2.14 | Testing and Commissioning of complete installation in accordance with SANS 10142-1 including the issue of COC certificates | Sum | 1
General
Lighting System Protection
C.2.15 | Design, Supply and install earthing, lightning, and fault protection for the entire installation | Sum | 1
Total Brought Forward
11kV MINIATURE SUBSTATION
C.2.16 | Design, Supply, deliver and install | Sum | 1
200kVA Type B 11.75/0.400 kV, 50 Hz, Dyn 11, 5% impedance, fault level rating of 30kA on MV side, fault level rating of 50kA on low voltage bus-bar, oil cooled ONAN, coastal type avocado green ‘C12’ mini-substation, complete with MV and LV switchgear compartments, protection relays, all current transformers, earthing material, Relay and Communication compartment, BTU, all other equipment, fixing materials
and accessories etc. The Mini Sub at minimum should also include a 2R2B RMU with fault protection all designed by the contractor
Design, supply and install of concrete plinth base for mounting the Minisub and should have a Five-sided cage structure (four vertical walls with security gates and a roof). The security mess panel cage system is to be constructed from mild steel and hot dip galvanized for marine environments as per SANS 121/BS EN ISO 1461. The gate system is to be secured with an approved padlock entry system. Clearance should be made so that the Kiosk doors can be opened for operations and maintenance. Clearances should be at minimum 1m on the sides of the Minisub and 2m on the front and back for the doors to open.
C.2.17 | Verify sizing, Supply, deliver and install 185mm2, 3 core, Cu, SWA, 6,35/11kV XLPE cable. Note: To be of the fire retardant, self-extinguishing type - (Red Stripe). Installation inclusive of all terminations required | m | 1500,00
C.2.18 | Provide a provisional amount of R200,000 for Alterations and additions required to connect the new Minisub to the Existing Culemborg Minisub RMU including cable tracing existing MV cable | Prov. Sum |  | 200000 | 200000
Total Carried Forward to Section Summary
Item | Description | Unit | Quantity | Rate | Amount
No.
Total Brought Forward
BILL NO.3
COMMISSIONING OF ELECTRICAL WORKS
C.3.1 | Illumination study (post installation) | Sum | 1
C.3.2 | Testing and Commissioning of complete installation in accordance with SANS 10142-1 including the issue of COC certificates | Sum | 1
END OF SECTION
Total Carried for Section Summary
BILL NO. | SECTION 3 SUMMARY | AMOUNT
C1 | BILL NO.1: ELECTRICAL DESIGN, VERIFICATION AND MODELLING
C2 | BILL NO 2: LIGHTING ENTRANCE LIGHTING
C3 | BILL NO.3: COMMISSIONING OF ELECTRICAL WORKS
| TOTAL EXCLUDING VAT | R
CARRIED TO FINAL SUMMARY

## Summary
THIS IS NOT A RETURNABLE DOCUMENT
Section | Summary | Amount (R)
1 | SECTION NO 1: PRELIMINARIES AND GENERAL
2 | SECTION NO. 2: CIVIL WORK
3 | SECTION NO.3: ELECTRICAL WORK
4 | SECTION NO.4: ESCALATION PROVISION IN TERMS OF 'CLAUSE X1' OF THE NEC | 2238000
TOTAL EXCLUDING VAT CARRIED TO FORM OF OFFER AND ACCEPTANCE