## BoQ
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription | Unit | Qty | Rate | Amount
1 |  | SECTION 1: PRELIMINARIES AND GENERAL
PREAMBLES
Fixed preliminary items
Fixed preliminary items will be valuated and paid on a proven cost basis up to the total value.
Time related preliminary items
Time related preliminary items may relate to fixed preliminary items and items not listed and expressed as a sum and will be pro-rated against value of construction items completed.
1.1 |  | FIXED PRELIMINARY ITEMS
Contractual requirements
1.1.1 |  | Contractual requirements, sureties, insurance, etc. | Sum | 1 |  | 0
0
|  | Establishment of facilities on site |  |  |  | 0
0
1.1.2 |  | Offices for Engineer & staff and notice board. | Sum | 1 |  | 0
0
1.1.3 |  | Notice boards, etc. | Sum | 1 |  | 0
0
|  | Facilities for the contractor |  |  |  | 0
0
1.1.4 |  | Tools and Equipment. | Sum | 1 |  | 0
0
1.1.5 |  | Workshops. | Sum | 1 |  | 0
0
1.1.6 |  | Ablutions and latrine facilities. | Sum | 1 |  | 0
0
1.1.7 |  | Water Supplies, electric power and communications. | Sum | 1 |  | 0
0
1.1.8 |  | Offices and storage sheds. | Sum | 1 |  | 0
0
1.1.9 |  | Dealing with dust. | Sum | 1 |  | 0
0
1.1.10 |  | Equipment. | Sum | 1 |  | 0
0
1.1.11 |  | Access. | Sum | 1 |  | 0
0
1.1.12 |  | Removal of site establishment. | Sum | 1 |  | 0
0
|  | Other Fixed-charge Obligations |  |  |  | 0
0
1.1.13 |  | Health and safety. | Sum | 1 |  | 0
0
1.1.14 |  | Environmental. | Sum | 1 |  | 0
0
1.1.15 |  | Dealing with traffic. | Sum | 1 |  | 0
0
1.1.16 |  | As-built surveys. | Sum | 1 |  | 0
0
1.1.17 |  | Security. | Sum | 1 |  | 0
0
TOTAL CARRIED FORWARD TO SECTION SUMMARY
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription | Unit | Qty | Rate | Amount
SECTION 1: PRELIMINARIES AND GENERAL
|  | As Built Documentation and Operating and Maintenance Manuals: |  |  |  | 0
0
1.1.18 |  | As Built Documentation and Operating and Maintenance Manuals. | Sum | 1 |  | 0
1.2 |  | TIME RELATED PRELIMINARY ITEMS |  |  |  | 0
0
|  | Time Related Preliminary obligations may relate to fixed preliminary items not listed |  |  |  | 0
0
1.2.1 |  | Time related obligations. | Sum | 1 |  | 0
TOTAL CARRIED FORWARD TO SECTION SUMMARY
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription |  |  | Page | Amount
SECTION 1: PRELIMINARIES AND GENERAL
SECTION SUMMARY
|  | Page Total brought forward |  |  | 1 | 0
|  | Page Total brought forward |  |  | 2 | 0
TOTAL CARRIED FORWARD TO FINAL SUMMARY
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription | Unit | Qty | Rate | Amount
2 |  | SECTION 2: CIVIL WORKS
2.1 |  | BILL NO. 1 - DEMOLITIONS,ETC
TRADE PREAMBLES
Trade Preambles:
For Trade Preambles refer to 'Model Preambles forTrades' (2008 edition) for the full descriptions of material to be used and work to be done in this Bill.
REMOVAL OF EXISTING WORK
2.1.1 |  | Asphalt surfacing (30mm thick). | m² | 223
2.4.2 |  | Remove existing Palisade Fence including gates, posts, bases, etc. | m | 54 |  | 0
2.1.3 |  | Remove existing Trackwork including Rails, Ballast and sleepers. | m | 10
2.1.4 |  | Remove Existing 150mm G5 and 150mm G2 Layerworks under asphalt trackwork. | m² | 223
Saw cutting existing surfaces, etc:
2.1.5 |  | Asphalt surfacing (30mm thick). | m | 111
2.2 |  | BILL NO. 2 - EARTHWORKS AND EXCAVATION
SITE CLEARANCE, ETC.
Site clearance:
2.2.1 |  | Digging up and removing rubbish, debris,vegetation, hedges, shrubs and trees n.e 200mm girth and cart away. | m² | 226 |  | 0
0
EXCAVATION, FILLING, ETC.
EXCAVATION, FILLING, ETC. OTHER THAN BULK
Digging up topsoil:
2.2.3 |  | Digging up topsoil to an average depth of 150mm and stockpiling on site including carting away to dumpsite selected by contractor. | m² | 226 |  | 0
0
Excavate in trenches n.e 2m deep:
2.2.4 |  | Hand excavation to determine existing services. | m³ | 40 |  | 0
0
2.2.5 |  | Excavate to reduce levels for layerworks. | m³ | 218 |  | 0
0
Extra over trenches and holes excavations:
2.2.6 |  | Soft rock 10%. | m³ | 25.8
2.2.7 |  | Hard rock 5%. | m³ | 12.9
Extra over all excavations for carting away:
2.2.8 |  | Surplus material from excavations and/or stock piles on site to a dumping site to be located by the Contractor. | m³ | 245
TOTAL CARRIED FORWARD TO SECTION SUMMARY
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription | Unit | Qty | Rate | Amount
2 |  | SECTION 2: CIVIL WORKS
Keeping excavations free from water:
2.2.9 |  | Keep excavations free from water. | Item | 1
FILLING ETC
Earth filling supplied by the Contractor:
0
2.2.10 |  | 150mm layer of G5 material compacted to 97% Mod AASHTO DENSITY. | m³ | 52
2.2.11 |  | 150mm layer of G2 material compacted to 97% Mod AASHTO DENSITY. | m³ | 52 |  | 0
0
Compaction of ground:
0
2.2.12 |  | Compaction of natural or excavated ground surface under floors etc, including scarifying for a depth of 150mm, breaking down oversize material, adding suitable material where necessary and compacting to 93% Mod AASHTO density. | m² | 197
0
Bituminous premix road surfacing:
2.2.13 |  | Bitumin spray to base course. | m² | 29
2.2.14 |  | 30mm thick asphalt. | m² | 29
2.3 |  | BILL NO. 3 - CONCRETE, FORMWORK AND REINFORCEMENT |  |  |  | 0
0
REINFORCED CONCRETE CAST ON/IN FORMWORK
30MPa/19mm Reinforced concrete:
2.3.1 |  | Pad Foundations. | m³ | 3
2.3.2 |  | Columns. | m³ | 1
2.3.3 |  | Plinths. | m³ | 90 |  | 0
0
2.3.4 |  | Formwork to sides of plinths. | m² | 69 |  | 0
|  | REINFORCEMENT |  |  |  | 0
Fabric reinforcement:
2.3.5 |  | Ref 888 fabric reinforcement mesh to plinths. | m² | 105 |  | 0
0
2.3.6 |  | Steel rod reinforcement (fnds and plinth). | t | 2.84 |  | 0
0
Test cubes:
2.3.7 |  | Making and testing 150x150x150mm concrete strength test cubes. | no | 56.4
Finishing top surfaces of concrete with power float:
2.3.8 |  | Plinths. | m² | 105
TOTAL CARRIED FORWARD TO SECTION SUMMARY
0
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription | Unit | Qty | Rate | Amount
SECTION 2: CIVIL WORKS
2.4 |  | BILL NO. 4 PRECAST CONCRETE |  |  |  | 0
0
Precast concrete finished smooth on exposed surfaces including bedding, jointing and pointing:
2.4.1 |  | U channel and cover. | m | 80 |  | 0
2.5 |  | BILL NO. 5 - PALISADE FENCING AND GATES
Note:
In high corrosion areas fence posts, stays, gates, etc are to be hot-dipped galvanised.
Fencing
Excavations other than bulk:
2.5.1 |  | Trenches. | m3 | 8
2.5.2 |  | Holes. | m3 | 4
Extra over excavations other than bulk in earth for excavation in:
2.5.3 |  | Soft rock 10% | m3 | 1.2
2.5.4 |  | Hard rock 5% | m3 | 0.6
2.5.5 |  | Compaction of excavated surfaces, adding suitable material where necessary and compact to 93% Mod AASHTO density. | m2 | 22
Extra over all excavations for loading, carting away and dumping:
2.5.6 |  | Surplus excavated material (no allowance made for increase in bulk) off site to a dumping site located by the contractor. | m3 | 11.28
Risk of collapse of excavations:
2.5.7 |  | To sides of trenches and holes not exceeding 1.5m deep. | m2 | 68
Keeping excavations free from water:
2.5.8 |  | Keeping excavations free from water. | Item | 1
Unreinforced concrete cast against excavated surfaces:
2.5.9 |  | 15Mpa/19mm stone Concrete. | m3 | 12
Finishing all exposed edges and corners of concrete:
2.5.10 |  | 20mm chamfers, sloping and splayed, etc. | m | 87.6
2.5.11 |  | Allow for signages including Transnet signage (provisional) | sum | 1
TOTAL CARRIED FORWARD TO SECTION SUMMARY
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription | Unit | Qty | Rate | Amount
SECTION 2: CIVIL WORKS
Hot dipped galvanized palisade fencing:
2.5.12 |  | Palisade fence 2400mm high comprising of 2375m high 40 x 40 x 3mm angle iron mitred spear head profile pales at 150mm centres (12 per 1950m section) in nominal panel size 1950m wide, with centre anti-sag pale 2,375m high, pales welded to and including 50 x 50 x 3mm angle section top and bottom rails, bolted to and including 100 x 55 x 2400mm I-Section hot dip galvanised IPE at 1950mm centres (SABS 121, ISO 1461 1999 specification) after welding of fish tail brackets to posts to receive rails, with top of post capped and seam welded and ground smooth prior to galvanizing and a 8mm drainage hole drilled 650mm from bottom of post, with M12 x 40mm (4No per 3m section) galvanised cup square bolt and high tensile anti-vandal shear nuts, posts are to be pre-holed prior to galvanising with 2 No 4mm diameters holes at 100mm centres (on internal face only) per post, both holes to be filled with a grey plastic/ nylon plug to prevent water penetration, rails fixed to post with and including 2No. 40 x 4mm a 250mm long fish plate brackets, both holes to be filled with a grey plastic/ nylon plug to prevent water penetration, rails fixed to intermediate post with and including 2No. 40 x 4mm a 250mm long fish plate brackets, bent around half of the post, to ensure adequate grip to the post, end brackets to be used where panels are stepped, and the bottom and top rails on the two ends fixed to brick piers with and including adequate brackets and suitable expansion bolts, posts are planted in a minimum of 15MPa 19mm concrete block 400 x 400 x 750mm deep foundation to be excavated to 850mm deep for top of foundation to be 100mm below natural ground level, including all necessary excavation, backfill, carting away, formwork etc installed complet. | no | 32
2.5.13 |  | Allow for Pedestrian Gate Size 1500mm wide x 2400mm high for the Palisade fence. | no | 1
2.6 |  | BILLL NO. 6 - STRUCTURA STEELWORK |  |  |  | 0
0
2.6.1 |  | Structural Steel staircase and platform. | t | 3 |  | 0
0
0
TOTAL CARRIED FORWARD TO SECTION SUMMARY
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription |  |  | Page | Amount
SECTION 2: CIVIL WORKS
SECTION SUMMARY
|  | Page Total brought forward |  |  | 4 | 0
|  | Page Total brought forward |  |  | 5 | 0
|  | Page Total brought forward |  |  | 6
|  | Page Total brought forward |  |  | 7
TOTAL CARRIED FORWARD TO FINAL SUMMARY
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription | Unit | Qty | Rate | Amount
3 |  | SECTION 3: ELECTRICAL WORKS
3.1 |  | BILL NO. 1 - ALTERATIONS AND ADDITIONS TO EXISTING ELECTRICAL INFRASTRUCTURE
3.1.1 |  | Alterations and addition to Existing Tug Jetty Extension Electrical Kiosk including installation of of 10mm² 4 Core PVC insulated PVC bedded ECC, SWA PVC sheathed 600/1000V cable. | no | 1 |  | 0 | Revised
0
3.2 |  | BILL NO. 2 - LOW VOLTAGE DISTRIBUTION |  |  |  | 0
0
3.2.1 |  | Design, supply, installation and commissioning of Surface Mounted Low Voltage Type 1 distribution IP69 kiosk as per drawing: in accordance to SANS10142-1. | no | 1 |  | 0 | Revised
0
3.2.2 |  | Design, and construction of concrete plinth. Contractor shall co-ordinate plinth details with the new LV Kiosk panel manufacturer. | no | 1 |  | 0 | Revised
0
3.3 |  | BILL NO. 3 - CABLE/WIREWAYS |  |  |  | 0
0
3.3.1 |  | Supply and Installation of 110mm uPVC sleevs, including trench. | m | 200 |  | 0 | Revised
0
3.4 |  | BILL NO. 4 - SUPPLY AND INSTALLATION OF LOW VOLTAGE CABLES |  |  |  | 0
0
3.4.1 |  | 10mm² 4 Core PVC insulated PVC bedded ECC, SWA PVC sheathed 600/1000V cable. | m | 80 |  | 0
0
3.5 |  | BILL NO. 5 - CABLE TERMINATIONS (ALL GLANDS SHALL BE IPLUS CORROSION GUARD) |  |  |  | 0
0
3.5.1 |  | Size 3 -M32, IP67 Corrosion Guard cable gland. | no | 2 |  | 0 | Revised
0
3.6 |  | BILL NO. 6 - MISCELLENEOUS ITEMS |  |  |  | 0
0
3.6.1 |  | Allowance for termination & junction boxes, adaptors, reducers and accessories. | Sum | 1 |  | 0
0
3.7 |  | BILL NO. 7 - TESTING AND COMMISSIONING |  |  |  | 0
0
3.7.1 |  | Testing and commissioning of complete Electrical Installation by a certified Electrician (including issuing of COC in accordance to SANS 10412-1). | no | 1 |  | 0 | Revised
0
0
0
0
|  | TOTAL CARRIED FORWARD TO SECTION SUMMARY |  |  |  | 0
0
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription |  |  | Page | Amount
SECTION 3: ELECTRICAL WORKS
SECTION SUMMARY
|  | Page Total brought forward |  |  | 9 | 0
|  | TOTAL CARRIED FORWARD TO FINAL SUMMARY |  |  |  | 0
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription | Unit | Qty | Rate | Amount
4 |  | SECTION 4: MECHANICAL WORKS
4.1 |  | BILL NO. 1 - DIESEL REFUELLING SYSTEM
Supply, delivery, installation and commissioning of the following self-bunded tank and stainless steel 316 piping, complete with valves, bends, tees, brackets, supports and all necessary accessories, as per the concept drawings:
4.1.1 |  | Self-bunded diesel storage tank, 75000L with all safety valves, level sensor and alarm, level indicator, thermostat, vent, and all necessary accessories. The tank shall be mounted on the concrete plinth as indicated on the drawing. | no | 1 |  | 0
0
4.1.2 |  | Galvanized mild steel platform to be bolted on concrete. | no | 1 |  | 0
0
4.1.3 |  | Self-priming centrifugal pump (KSB, Gorman, Turbofluid, or similar approved), flowrate 450 L/min, power input 5.5 kW at 380 V. The pump shall comply with zone 1 requirements including spark proof motor. | no | 2 |  | 0
0
4.1.4 |  | Pipe, DN 80: stainless steel 316 pipe. | m | 2 |  | 0 | Revised
0
4.1.5 |  | Pipe, DN 65: stainless steel 316 pipe. | m | 190 |  | 0 | Revised
0
4.1.6 |  | Pipe, DN 25: stainless steel 316 pipe. | m | 2 |  | 0 | Revised
0
4.1.7 |  | Tee, DN 65 x DN 65: stainless steel 316 pipe. | m | 10 |  | 0 | Revised
0
4.1.8 |  | DN 65, 90 degree: stainless steel 316 bends. | no | 26 |  | 0
0
4.1.9 |  | DN 25, 90 degree: stainless steel 316 bends. | no | 2 |  | 0
0
4.1.10 |  | DN 80 x DN 65: stainless steel 316 reducer. | no | 2 |  | 0
0
4.1.11 |  | DN 65 x DN 25: stainless steel 316 reducer. | no | 4 |  | 0
0
4.1.12 |  | Pressure relief valve, DN 65: stainless steel 316. | no | 2 |  | 0
0
4.1.13 |  | Basket strainer, DN 65: stainless steel 316. | no | 2 |  | 0
0
4.1.14 |  | Ball valve, DN 65: stainless steel 316. | no | 10 |  | 0
0
4.1.15 |  | Check valve (non-return valve), DN 65: stainless steel 316. | no | 4 |  | 0
0
4.1.16 |  | Pressure gauge, 63 mm diameter - 8 mm connection pipe. | no | 2 |  | 0
0
4.1.17 |  | Temperature gauge, 89 mm stem - 20 mm connection pipe. | no | 2 |  | 0
0
4.1.18 |  | Flow meter, 567 L/min maximum flow with meter, register, strainer, preset valve, counter and air eliminator. | no | 2 |  | 0
0
4.1.19 |  | Diesel filter with 10 micro, filter cartridge. | no | 1 |  | 0
0
4.1.20 |  | Coupling, DN 65 dry break male dust cap. | no | 1 |  | 0
0
4.1.21 |  | Bonding cable on manual reel and clamp. | sum | 1 |  | 0
0
4.1.22 |  | Pipe supports including hot dip galvanized 50 x 50 angle iron and 6mm plate, S/S 316 U-bolts, S/S 316 anchor bolts, S/S 316 nuts and S/S 316 washers as indicated on the drawings. | sum | 1 |  | 0
0
TOTAL CARRIED FORWARD TO SECTION SUMMARY
0
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription | Unit | Qty | Rate | Amount
SECTION 4: MECHANICAL WORKS
4.1.23 |  | Electrical control panel and Instrumentation Including DB enclosure, contactor, overload, fuses, start and stop buttons (pump control), emergency stop, cable rack, internal wiring and schematic diagram. | no | 1 |  | 0 | Revised
4.1.24 |  | Design and deliver a portable refueling station with an HDG trolley, fuel flow meter, 15m long automatic rewinding hose reel, refueling nozzle, pump start/stop control panel, and emergency stop buttons as per the specifications. | no | 1 |  | 0 | Revised
0
4.1.25 |  | DN 65 Flexible stainless steel braided hose, both ends of the hose shall be fitted with an API 100 female dry break coupler. | m | 15 |  | 0
0
4.1.26 |  | Spill kit suitable to clean up a spill of approximately 60 liters which shall comprise of 30 liters Biozorb peat fibre, 2m boizorb boom, biozorb cushion, 15 off 200 gram oil absorbent pads, one pair gloves and mask, one anti-mist goggles, three heavy duty disposal bags and ties, one each spark proof broom and shovel. | no | 1 |  | 0
0
4.1.27 |  | Underground Piping: Corrosion protection in the form of plastic wrapping of the steel pipelines shall be performed in accordance with SANS 10129 (Latest edition) “Plastic Tape Wrapping of Steel Pipelines”. | m | 50 |  | 0
0
4.1.28 |  | Aboveground Piping: 1st layer – Epoxy powder spray-applied with electrostatic guns in typical thickness of 80 – 250 μm. 2nd layer – Copolymer bonding layer extruded in typical thickness of 250 μm. 3rd layer – Outer polyethylene layer extruded in typical thickness of 1.2 – 3.5 mm, | m | 110 |  | 0
0
4.1.29 |  | 2x Operator and 2x maintenance staff training in the operation and the maintenance of the refuelling plant. | sum | 1 |  | 0
0
4.1.30 |  | Acceptance test on the complete plant shall be conducted by the Contractor in the presence of the Employer’s representative. The plant will only be accepted by the Employer once the successful operation of the plant has been demonstrated by the Contractor to the satisfaction of the Employer. | sum | 1 |  | 0
0
4.1.31 |  | Maintenance and operating instructions handbooks. | sum | 1 |  | 0
0
0
4.2 |  | BILL NO. 2 - FIRE PROTECTION SYSTEM |  |  |  | 0
0
|  | Supply, delivery and installation and commissioning of the following fire protection system, complete with fire extinguishers, portable foam monitor, and all related signage, brackets, supports and all necessary accessories, as per the concept drawings: |  |  |  | 0
0
4.2.1 |  | Portable Extinguishers: 6.8kg dry chemical powder fire extinguishers with mounting brackets and associated accessories. | no | 3 |  |  | Revised
4.2.2 |  | Portable Extinguishers: 9kg carbon dioxide fire extinguishers with mounting brackets and associated accessories. | no | 3 |  | 0 | Revised
0
4.2.3 |  | Hose Boxes: Hose boxes completed with two (2) 30m with 30mm couplers and branch pipes including mounting brackets. | no | 1 |  |  | Revised
0
4.2.5 |  | Fire safety signs and warning signs. | sum | 1 |  | 0 | Revised
0
|  | TOTAL CARRIED FORWARD TO SECTION SUMMARY |  |  |  | 0
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription |  |  | Page | Amount
SECTION 4: MECHANICAL WORKS
SECTION SUMMARY
|  | Page Total brought forward |  |  | 11 | 0
|  | Page Total brought forward |  |  | 12
|  | TOTAL CARRIED FORWARD TO FINAL SUMMARY |  |  |  | 0
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription | Unit | Qty | Rate | Amount
SECTION 5: PROVISIONAL SUMS
5.1 |  | BUDGETARY ALLOWANCES
5.1.1 |  | Provide an amount of R50 000 (Fifty Hundred Thousand Rands Only) for the removal of contaminated material. | Item | 1 | 50000 | 50000
5.1.2 |  | Provide an amount of R50 000 (Fifty Thousand Rands Only) for the removal of existing services. | Item | 1 | 50000 | 50000
5.1.3 |  | Provide an amount of R 100 000 (One Hundred and Thousand Rands Only) for De-watering. | Item | 1 | 100000 | 100000
5.1.4 |  | Provide an amount of R 100 000.00 (One Hundred Thousand Rands Only) for Geotechnical Investigation and Tank Foundation Design. | Item | 1 | 100000 | 100000
5.1.5 |  | Provide an amount of R50 000 (Fifty Thousand Rands Only) for service detection which includes the utilies detection, instrumentation and the reoprt. | Item | 1 | 50000 | 50000
.
5.1.6 |  | Provide an amount of R60 000 (Sixty Thousand Rands Only) for 2 x Manholes including covers as per DRWNG No. XDN.E.0053-000-C-DE-0002-01-0A-SM. | Item | 1 | 60000 | 60000
0
TOTAL CARRIED FORWARD TO FINAL SUMMARY
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription |  |  | Page | Amount
SECTION 5: PROVISIONAL SUMS
SECTION SUMMARY
|  | Page Total brought forward |  |  | 14
|  | TOTAL CARRIED FORWARD TO FINAL SUMMARY |  |  |  | 0
0
TRANSNET NATIONAL PORTS AUTHORITY
CONTRACT NUMBER : TBA
DESCRIPTION OF THE WORKS: PROPOSED DIESEL STORAGE TANK AT THE TUG JETTY IN THE PORT OF DURBAN
Item | Payment Clause | Discription |  |  | Page | Amount
BILL OF QUANTITIES
FINAL SUMMARY
|  | SECTION 1: PRELIMINARY AND GENERAL |  |  | 3 | 0
|  | SECTION 2: CIVIL WORKS |  |  | 8 | 0
|  | SECTION 3: ELECRICAL WORKS |  |  | 10 | 0
|  | SECTION 4: MECHANICAL WORKS |  |  | 13
|  | SECTION 5: PROVISIONAL SUMS |  |  | 15
|  | TOTAL EXCLUDING VAT CARRIED FORWARD TO FORM OF OFFER AND ACCEPTANCE |  |  |  | 0

## Fly Sheets - Prelims
SECTION 1: PRELIMINARIES
0

## Fly Sheets - Civil Works
SECTION 2: CIVIL WORKS
0

## Fly Sheets - Electrical Works
SECTION 3: ELECTRICAL WORKS
0

## Fly Sheets - Mechanical Works
SECTION 4 MECHANICAL WORKS
0

## Fly Sheets - Provisional Sums
SECTION 5 PROVISIONAL SUMS
0

## Final Summary
FINAL SUMMARY
0